SECTION 23 00 00

Analog Transmitter
Analog Transmitter, Programmable, Model 310

PART 1 - GENERAL

  - SCOPE

- This section describes the requirements for an analog transmitter.

- Under this item, the contractor shall furnish and install the flow measurement equipment and accessories as indicated on the plans and as herein specified.

  - SUBMITTALS

- The following information shall be included in the submittal for this section:

- Outline dimensions, conduit entry locations and weight

- Customer connection and power wiring diagrams

- Data sheets and catalog literature for programmable analog transmitter

- Interconnection drawings

- Installation and operations manual

- List of spare parts

- Complete technical product description including a complete list of options provided

- Any portions of this specification not met must be clearly indicated or the supplier and contractor shall be liable to provide all additional components required to meet this specification

  - SYSTEM DESCRIPTION

- The programmable analog transmitter shall accept relatively fast, unscaled raw pulses from a flow sensor (or similar device), and then transmit a linear analog signal. The scale and units of measure shall be customizable.

  - DEFINITIONS

- Loop-powered – A device that can be connected to a current loop and powered without the need of a separate power source.

- Raw Pulse Output – A signal wave generated by a sensor. Must be converted before it is usable.

- Linear Analog Signal – A wave form that is a linear output of its inputs.

- NEMA 4X – A type of enclosure designed for outdoor use that offers good protection against corrosion and extreme elements.

PART 2 – PRODUCTS

  - APPROVED MANUFACTURERS

Basis-of-Design Product: Subject to compliance with specifications, provide programmable analog transmitter by one of the following:

Impeller by Badger Meter

  - OPERATING CONDITIONS

- Operational Requirements

- Programmable Analog Transmitter

- The Programmable Analog Transmitter is a loop-powered, programmable 4-20mA transmitter designed to accept relatively fast, unscaled raw pulses from devices like flow sensors, and then transmit a linear analog signal of desired scaling and units of measure. In addition to our standard flow sensors, the Model 310 can also accept a sine wave, making it a 
versatile transmitter.

- Operating Principle: The Programmable Analog Transmitter receives a signal from a flow meter (or similar device), converts it to a usable output, and then transmits it through the output cables.

- Input

- The input signal shall be a relatively fast, unscaled raw pulse signal from a flow meter or another similar device.

- Frequency: 0.4…10kHz

- Load resistance: Max. 750 Ω at 24V DC

- Output

- The output signal shall be a linear analog signal. The scale and units of measure shall be customizable.

- Output strength: 4…20 mA

- Output response time: Varies with filter

- System Performance

- Accuracy shall be ±0.04% of reading over entire span

- Linearity shall be 0.1% of full scale

- Power Requirements

- Loop input voltage: 9…35V DC

- Integrations

- Model RED Totalizing Display

- Model 310 Programming Kit

PART 3 - EXECUTION

  - INSTALLATION

- Follow manufacturer’s recommendation for installation and conform to the guidelines provided by the Installation and Operation Manual.

- The transmitter shall be calibrated using windows based software connected to the D.I.C. Comm port. The transmitter must be calibrated before it can transmit a useful signal.

- The transmitter shall be mounted on a surface using tape or fasteners, on a DIN rail, or on a wall using an enclosure. The enclosure shall be a NEMA 4x Plastic Enclosure, a Metal Enclosure, or a Plastic Enclosure.

- Connect cables according to instructions in the Installation and Operation Manual.

  - PRODUCT SUPPORT

- For additional information on the product, please visit our website, call toll-free, or contact us via email.

      - Web: BadgerMeter.com

      - Tel: 800-876-3837

      - Email: infocentral@badgermeter.com

  - MANUFACTURER’S WARRANTY

- Terms

- See manufacturer’s website: Warranty

END OF SECTION