SECTION 23 00 00

340N2
BTU Transmitter, Model 340N2

GENERAL

SCOPE

This section describes the requirements for a BTU transmitter.

Under this item, the contractor shall furnish and install the flow measurement equipment and accessories as indicated on the plans and as herein specified.

SUBMITTALS

- The following information shall be included in the submittal for this section:

- Data sheets and catalog literature for flow sensor

- Installation and operations manual

- List of spare parts

- Complete technical product description including a complete list of options provided

- Any portions of this specification not met must be clearly indicated or the supplier and contractor shall be liable to provide all additional components required to meet this specification

SYSTEM DESCRIPTION

The Model 340N2 transmitter works in conjunction with a flow sensor and two temperature sensors to calculate thermal energy by measuring liquid flow and inlet and outlet temperatures in a closed pipe system.  The transmitter requires two 10 kΩ thermistors for temperature input.  The transmitter can accept the signal from most Badger Meter raw pulse flow sensors, as well as many other pulse and sine wave devices.

The onboard microcontroller and digital circuitry make precise measurements and produce accurate, drift-free outputs.  The Model 340N2 transmitter is configured using Badger Meter Windows® based programming software.  Calibration information for the flow sensor, units of measurement and output scaling may be preselected or entered in the field.  Btu transmitter information is available when connected to a PC or laptop computer.  This information includes real-time flow rate, flow total, both T1 and T2 temperature probe information, energy rate, and energy total.

DEFINITIONS

BTU – (British Thermal Unit) A unit of heat, often used in HVAC. 1 BTU is the amount of heat required to raise the temperature of one pound of water by one degree Fahrenheit.

Thermistor – A type of resistor where the resistance is based on temperature. Useful for temperature sensing.

PRODUCTS

APPROVED MANUFACTURERS

Basis-of-Design Product: Subject to compliance with specifications, provide flow measurement technology by one of the following:

Badger Meter

OPERATING CONDITIONS

Operational Requirements

BTU Transmitter

Power Supply

12…35V DC ±5%

12…24V AC ±10%

Current Draw

60 mA at 12V DC

Pulse Sensor Input

Signal Amplitude

2.5V DC threshold

Signal Limits

Vin < 35V (DC or AC peak)

Frequency

0.4…1.0 kHz

Pull-up

To 9.1V DC with 2 kΩ

Sine Wave Sensor Input

Signal Amplitude

10 mV p-p threshold

Signal Limits

Vin < 35V (DC or AC peak)

Frequency

0.4…1.0 kHz

Temperature Sensor Input

Two required

10 kΩ thermistor

2-wire

Type II

10 kΩ at 77° F (25° C)

Pulse Output

Opto-isolated solid state switch

Voltage range

0…±60V (DC or AC peak)

Closed (on) state

Load current, 700 mA max. over operating temperature range

On-resistance, 700 mΩ max. over operating temperature range

Open (off) state

Leakage at 158° F (70° C) <1µA at 60V (DC or AC peak)

N2 Output

RS-485 output compliant with EIA/TIA-485 standards

Operating Temperature

–20...158° F (–29...70° C)

Storage Temperature

–40...185° F (–40...85° C)

Weight

4.8 oz with headers installed

EXECUTION

INSTALLATION

Follow manufacturer’s recommendation for installation and conform to the guidelines provided by the Installation and Operation Manual.

MANUFACTURER’S WARRANTY

Terms

The manufacturer of the above specified equipment shall guarantee for twelve (12) months from date of installation; or one (1) year and six (6) months after the date of shipment that the equipment shall be free from defects in design, workmanship or materials.

END OF SECTION